## Inputs & Outputs
INPUTS to Standby Rate Estimator (for Con Edison Rates)
1) Facility Information:
| Rate Class/Voltage Level | [6 empty] | Facility Type
| Site Location | [6 empty] | Does Site Use Electric Chilling? | Tables!$G$52
2) Energy Consumption Information:
(You should find these data on your monthly bill.) |  |  |  |  | Peak kW Demand |  | Monthly kWh |  | Commodity Prices |  | Total Bill
[5 empty] | Mo. Peak | Per. 2 | Peak or Total | Off-Peak | On-Peak | Off-Peak | To Check
Demand: | Enter kW peaks in left columns |  |  | Jan | 470 | 470 | 85000 | 67000 | 0.12 | 0.08 | 1
|  |  |  | Feb | 470 | 470 | 85000 | 67000 | 0.12 | 0.08 | 333333
Energy: | kWh used in green columns |  |  | Mar | 470 | 470 | 85000 | 67000 | 0.11 | 0.09 | 1
|  |  |  | Apr | 460 | 460 | 144000 | 50000 | 0.1 | 0.08 | 44444
Prices: | $/kWh in yellow column(s) |  |  | May | 500 | 500 | 108000 | 50000 | 0.11 | 0.07 | 1
|  |  |  | Jun | 501 | 501 | 108000 | 50000 | 0.12 | 0.07 | 1
Contract Demand: |  | 500 | kW | Jul | 1001 | 1001 | 108000 | 50000 | 0.13 | 0.09 | 1
| (Your 12 month Peak is: | 1001 | KW) | Aug | 500 | 500 | 108000 | 50000 | 0.14 | 0.09 | 1
|  |  |  | Sep | 500 | 500 | 108000 | 50000 | 0.11 | 0.08 | 1
Average Demand Factor: |  |  |  | Oct | 460 | 460 | 85000 | 48000 | 0.11 | 0.08 | 1
| Estimate from Part 1: | 0% |  | Nov | 470 | 470 | 85000 | 67000 | 0.12 | 0.1 | 1
|  |  |  | Dec | 470 | 470 | 85000 | 67000 | 0.12 | 0.1 | 1
3) CHP Project Information
[9 empty] | Parasitic Load | 5%
| Nameplate capacity: |  |  | 300 | kW |  |  |  | Minimum Draw from Grid (kW) | 1
| Planned Operation: | [7 empty] | Planning to generate LESS than 15% of site load?
| In-Service Date: |  |  | 2009-03-06 |  |  |  |  | Planning to use Designated Technology?
(See Manual for Designated Technology Rules)
OUTPUTS (Estimates for Con Edison Service Area)
I. Qualitative Warnings and Notes
| Facility/Demand Data Input |  |  | User must select building type in section (1) or enter a Demand Discount Factor
| Contract demand Level |  |  | Contract Demand May be Too Low--Check Input Level
| Small Size (< 15% of load?) |  |  | N/A
| Small Size (b) |  |  | N/A
| Oversized |  |  | DG may be oversized--consider a smaller generator
| Designated Technology Exemption? |  |  | If project qualifies, you may choose which rate to use
| Designated Tech. Exemption Date? |  |  | Exemption Possible - is technology Designated?
| Eligible for Phase-in? |  |  | Eligible - See Estimates Below
II. Rate Estimates
% Change in Delivery Charges |  |  |  | With the proposed CHP Project:
CHP on Standby v. Current Charges |  |  | d | Select building type in section (1) or enter a Demand Discount Factor
CHP on Standard v. Current Charges |  |  | - | Select building type in section (1) or enter a Demand Discount Factor
CHP on Standby v. CHP on Standard |  |  | - | Select building type in section (1) or enter a Demand Discount Factor
Estimates With CHP | [7 empty] | Without CHP - Base Case
Invalid - Missing Data! |  |  | Standard Rate Estimate |  |  |  |  | Standard Rate Estimate
Basic Standby Charges |  |  | Basic Standard Charges |  |  |  |  | Basic Standard Charges
| Customer Chg. | - |  | Demand Chg. | 55389.38 |  |  |  | Demand Chg. | 113814.38
| Contract Dem. | - |  | Volumetric Chg. | 3961.4 |  |  |  | Volumetric Chg. | 21773.2
| As-Used Dem. | -
| Delivery Subtotal | 0 |  | Delivery Subtotal | 59350.78 |  |  |  | Delivery Subtotal | 135587.58
| MAC charges | - |  | MAC charges | 8781.31 |  |  |  | MAC charges | 25452.46
| Delivery w/ MAC | 0 |  | Delivery w/ MAC | 68132.09 |  |  |  | Delivery w/ MAC | 161040.04
Energy Commodity (kWh) |  |  | Energy Commodity (kWh) |  |  |  |  | Energy Commodity (kWh)
| On-Peak | 44695.45 |  | On-Peak | 44695.45 |  |  |  | On-Peak | 139780
| Off-Peak | 57990 |  | Off-Peak | 57990 |  |  |  | Off-Peak | 57990
| Commodity | 102685.45 |  | Commodity | 102685.45 |  |  |  | Commodity | 197770
SBC & RPS |  | 2456.791 | SBC & RPS |  | 2456.791 |  |  | SBC & RPS |  | 4317.1
Estimate: | ----------------- |  | Estimate: | 173274.331 |  |  |  | Estimate: | 363127.14
As-Used High-Low Range | [7 empty] | Actual Current Bill
| As-Used | Tot. Delivery | [5 empty] | (Compare with Standard w/o CHP)
High Case | 123428.0046 | #VALUE! | [5 empty] | Sum of Actual Bills: |  | 377787
Low Case | 0 | #VALUE! | [5 empty] | % Difference: |  | -3.88%
Estimator understates annual charges by 4%
Eligible | for Phase-In
Phase-In Computations | [6 empty] | Possible Additional Savings with Chilling
Year | % Standby | Std. Deliv. | SB Deliv. | Est. Pymnt |  |  | Summer Demand Offset (kW 'shaved') |  |  | 30 kW
Before 2008 | 0% | 0 | 0 | 0 |  |  | kWh Commodity Savings |  |  | 35,640 kWh
2008 | 25% | 0 | 0 | 0 |  |  | Estimated Standby Savings ($) |  |  | 48,348
2009 | 50% | 0 | 0 | 0 |  |  | Estimated Standard Rate Savings ($) |  |  | 12,338
2010 | 75% | 0 | 173274.331 | 0 |  |  | % Standby Delivery Savings |  |  | 101.1%
2011 and on | 100% | 0 | 173274.331 | 0 |  |  | % Standard Delivery Savings |  |  | 12.83%
Note on G10: Column autofills with Monthly Peak values--no need to enter. For most customers this assumption provides an equivalent result: most users should let Excel enter these Period 2 values. (Entering more detailed information may allow a more accurate standby estimate, if information is available.)
Note on H10: If you do not have off-peak kWh values fill this column with your total kWh and Estimator will (invisibly & automatically) impute on & off peak consumption. If you do have on and off peak data, fill this with peak consumption only.
Note on I10: If you do not have off-peak kWh values leave blank and Estimator will (invisibly & automatically) impute on & off peak consumption.
Note on K10: If on and off-peak information is not available, enter the average monthly cost in the "On-Peak" column, and leave this column blank. (In this case Estimator will estimate adjustments to create on and off-peak commodity cost values.)
Note on B17: Total site size, or maximum potential peak. (Maximum monthly kW shown for convenience in orange)
Note on B20: What percentage of peak demand less is the site's average demand? (Allows estimate of as-used demand levels.) No entry is necessary. See manual for explanation.
Note on C21: Value determined automatically by building type selection above. User override is possible, but once the formula is deleted it must be re-written manually. The Excel formula is: INDEX(Tables!O40:O46,Tables!P40,1)
Note on E30: mm/dd/yyyy Enter the projected date of initial operation.
Note on J30: See Manual for Designated Technology Rules
Note on B36: kW Contract Demand level should usually be set at maximum demand level.
Note on B38: If user plans a small unit but genset is 15% of load or smaller, then a warning is issued.
Note on B39: Warns if Nameplate capacity exceeds the product (Contract Demand Level * Avg. Demand Discount Factor). Even if warning is not triggered the project may be oversized; your engineer should fully consider all relevant factors.
Note on C47: Compares delivery charges only--not commodity energy costs.
Note on B71: Assumes 0% reliability & all peak day kW = monthly peak. Max theoretical as-used charges (Avg. Demand = 100% of monthly peak).
Note on C71: This remainder = Customer Charges + Contract Demand Charges.
Note on B72: Assumes as-used demand is always zero): CHP meets all peak demand and/or site never uses grid power during peak hours.
Note on H75: Conditional Outputs: Possible ADDITIONAL tariff savings by offsetting electric chiller load with CHP, only appear if customer indicates electric chillers are in use. Assumes 10% of genset nameplate rating (set in Tables page).
YES
This spreadsheet should be used in conjunction with the Standby Rate Manual: see www.xxxxxxxxxxxxxxxxxx
YES
YES

## Tables
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46
|  |  | Standby Rates | [10 empty] | OASC Rates | [20 empty] | 100 | <--ConEd tariffs show energy in cents/kWh; convert $$
Tariff Drop Down List Data |  |  | 1: Standby Rates; 7: Standby MAC; 12: OASC Demand ($/kW); 30: OASC Energy ($/kWh); 43: SBC; 44: RPS; 45: Tax
[5 empty] | Summer |  | Winter | [6 empty] | Summer |  |  |  | Winter |  |  |  | kW Block Size |  |  |  | Summer |  |  | Winter |  |  | Summer |  | Winter |  | kWh Block Size |  | Summer |  |  | Winter |  |  |  | SBC | RPS | NYC | Westchester
| 8 |  | Cust Chg | CD Chg | As-Use 1 | As-Use 2 | As-Use 1 | As-Use 2 | MAC Cust | MAC CD | MAC AU1 | MAC AU2 |  | Block 1 | Block 2 | Block 3 | Block 4 | Block 1 | Block 2 | Block 3 | Block 4 | Block 1 | Block 2 | Block 3 | Block 4 | Period 1 | Period 2 | All | Period 1 | Period 2 | All | Block 1 | Block 2 | Block 1 | Block 2 | Block 1 | Block 2 | Period 1 | Period 2 | All Other | Period 2 | All Other |  |  | $/kWh | $/kWh | % | %
UPDATED | SC-4_Rate_I |  | 1: 207.43; 2: 5.26; 3: 0.3369; 4: 0.7225; 6: 0.5024; 12: 18.79; 13: 17.88; 14: 16.99; 15: 15.86; 16: 14.93; 17: 14.03; 18: 13.13; 19: 12.01; 20: 100; 21: 800; 22: 1100; 23: Up; 30: 0.0152; 31: 0.0152; 32: 0.0152; 33: 0.0152; 34: 800000; 35: Up; 43: 0.0017; 44: 0.0006
2008-05-27 | SC-4_Rate_II |  | 1: 831.93; 2: 5.69; 3: 0.3264; 4: 0.6829; 6: 0.5128; 24: 5.67; 25: 10.52; 26: 11.87; 28: 7.79; 29: 3.78; 37: 0.0058; 38: 0.0058; 39: 0.0058; 40: 0.0058; 43: 0.0017; 44: 0.0006
| SC-4_Rate_III |  | 1: 207.43; 2: 5.26; 3: 0.3369; 4: 0.7225; 5: 0; 6: 0.5024; 24: 5.79; 25: 12.51; 26: 11.39; 28: 9.08; 29: 2.98; 37: 0.0058; 38: 0.0058; 39: 0.0058; 40: 0.0058; 43: 0.0017; 44: 0.0006
| SC-8_Rate_I |  | 1: 248.13; 2: 4.75; 3: 0.3427; 4: 0.8042; 6: 0.5022; 12: 19.38; 13: 17.93; 16: 15.17; 17: 13.72; 20: 100; 21: Up; 30: 0.012; 31: 0.012; 32: 0.012; 33: 0.012; 34: Up; 43: 0.0017; 44: 0.0006
| SC-8_Rate_II |  | 1: 886.8; 2: 4.75; 3: 0.349; 4: 0.8091; 6: 0.4852; 24: 5.06; 25: 9.75; 26: 12.36; 28: 6.47; 29: 4.53; 37: 0.0058; 38: 0.0058; 39: 0.0058; 40: 0.0058; 43: 0.0017; 44: 0.0006
| SC-8_Rate_III |  | 1: 248.13; 2: 4.75; 3: 0.3427; 4: 0.8042; 5: 0; 6: 0.5022; 24: 5.02; 25: 12.09; 26: 11.12; 28: 8.91; 29: 3.48; 37: 0.0058; 38: 0.0058; 39: 0.0058; 40: 0.0058; 43: 0.0017; 44: 0.0006
| SC-9_Rate_I |  | 1: 56.21; 2: 4.75; 3: 0.3528; 4: 0.6997; 6: 0.4213; 12: 15.44; 13: 13.94; 16: 12.34; 17: 10.83; 20: 900; 21: Up; 30: 0.0165; 31: 0.0165; 32: 0.0165; 33: 0.0165; 34: 15000; 35: Up; 43: 0.0017; 44: 0.0006
| SC-9_Rate_II |  | 1: 908.12; 2: 5.41; 3: 0.3423; 4: 0.691; 6: 0.52; 24: 5.86; 25: 11.09; 26: 10.94; 28: 8.14; 29: 3.54; 37: 0.0058; 38: 0.0058; 39: 0.0058; 40: 0.0058; 43: 0.0017; 44: 0.0006
| SC-9_Rate_III |  | 1: 56.21; 2: 4.75; 3: 0.3528; 4: 0.6997; 5: 0; 6: 0.4213; 24: 5.58; 25: 11.99; 26: 11.48; 28: 7.69; 29: 3.3; 37: 0.0058; 38: 0.0058; 39: 0.0058; 40: 0.0058; 43: 0.0017; 44: 0.0006
| SC-12_Rate_I |  | 1: 84.92; 2: 4.86; 3: 0.2498; 4: 0.5991; 6: 0.3665; 12: 16.18; 13: 14.49; 16: 9.46; 17: 7.77; 20: 200; 21: Up; 30: 0.0115; 31: 0.0115; 32: 0.0115; 33: 0.0115; 34: Up; 43: 0.0017; 44: 0.0006
| SC-12_Rate_II |  | 1: 416.46; 2: 4.76; 3: 0.291; 4: 0.6306; 6: 0.4298; 24: 4.27; 25: 8.31; 26: 9.13; 28: 4.35; 29: 7.05; 37: 0.0058; 38: 0.0058; 39: 0.0058; 40: 0.0058; 43: 0.0017; 44: 0.0006
| SC-12_Rate_III |  | 1: 84.92; 2: 4.86; 3: 0.2498; 4: 0.5991; 5: 0; 6: 0.3665; 24: 3.55; 25: 8.65; 26: 8.9; 28: 3.72; 29: 6.73; 37: 0.0058; 38: 0.0058; 39: 0.0058; 40: 0.0058; 43: 0.0017; 44: 0.0006
|  |  | Standby MAC Rates | [7 empty] | OASC MAC Rates
MAC Drop Down List Data |  |  | 1: NYC; 5: Westchester; 9: OASC MAC - NYC; 15: OASC MAC - Westchester; 24: SBC; 25: RPS
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 |  |  |  | 0.17 | 0.06
| 8 |  | MAC Cust | MAC CD | MAC AU1 | MAC AU2 | MAC Cust | MAC CD | MAC AU1 | MAC AU2 | kW - P1 | kW - P2 | kW - All | kWh-Pk | kWh-Off | kWh-All | kW - P1 | kW - P2 | kWh-Pk | kW - All | kWh-Off | kWh-All |  |  |  | (Cents/kWh)
| SC-4_Rate_I |  | 85.2392 | 2.0225 | 0.02325 | 0.20841 | 85.2392 | 2.0225 | 0.02325 | 0.20841 |  |  | 3.69 |  |  | 0.012 |  |  | 3.69 |  |  | 0.012
| SC-4_Rate_II |  | 301.0058 | 1.7117 | 0.014067 | 0.15533 | 301.0058 | 1.7117 | 0.014067 | 0.15533 | 1.39 | 1.6 |  | 0.008 | 0.005 |  | 1.39 | 1.6 |  | 0.008 | 0.005
| SC-4_Rate_III |  | 85.2392 | 2.0225 | 0.02325 | 0.20841 | 85.2392 | 2.0225 | 0.02325 | 0.20841 | 3.13 | 4.5 |  | 0.008 | 0.005 |  | 3.13 | 4.5 |  | 0.008 | 0.005
| SC-8_Rate_I |  | 67.5867 | 1.5433 | 0.023808 | 0.17898 | 67.5867 | 1.5433 | 0.023808 | 0.17898 |  |  | 2.55 |  |  | 0.009 |  |  | 2.55 |  |  | 0.009
| SC-8_Rate_II |  | 168 | 1.0816 | 0.0099667 | 0.13297 | 168 | 1.0816 | 0.0099667 | 0.13297 | 0.233 | 0.9 |  | 0.009 | 0.005 |  | 0.233 | 0.9 |  | 0.009 | 0.005
| SC-8_Rate_III |  | 67.5867 | 1.5433 | 0.023808 | 0.17898 | 67.5867 | 1.5433 | 0.023808 | 0.17898 | 0.803 | 3.2 |  | 0.009 | 0.005 |  | 0.803 | 3.2 |  | 0.009 | 0.005
| SC-9_Rate_I |  | 19.8592 | 1.2283 | 0.018017 | 0.12329 | 19.8592 | 1.2283 | 0.018017 | 0.12329 |  |  | 1.9 |  |  | 0.009 |  |  | 1.9 |  |  | 0.009
| SC-9_Rate_II |  | 377.1383 | 1.7867 | 0.015783 | 0.17943 | 377.1383 | 1.7867 | 0.015783 | 0.17943 | 1.23 | 1.5 |  | 0.008 | 0.005 |  | 1.23 | 1.5 |  | 0.008 | 0.005
| SC-9_Rate_III |  | 19.8592 | 1.2283 | 0.018017 | 0.12329 | 19.8592 | 1.2283 | 0.018017 | 0.12329 | 1.74 | 2.2 |  | 0.008 | 0.005 |  | 1.74 | 2.2 |  | 0.008 | 0.005
| SC-12_Rate_I |  | 65 | 1.38 | 0.018925 | 0.12119 | 65 | 1.38 | 0.018925 | 0.12119 |  |  | 0.86 |  |  | 0.009 |  |  | 0.86 |  |  | 0.009
| SC-12_Rate_II |  | 112 | 0.8 | 0.013 | 0.081 | 112 | 0.8 | 0.013 | 0.081 | 0.905 | 0 |  | 0.008 | 0.005 |  | 0.905 | 0 |  | 0.008 | 0.005
| SC-12_Rate_III |  | 65 | 1.38 | 0.016248 | 0.12119 | 65 | 1.38 | 0.016248 | 0.12119 | 3.13 | 1.1 |  | 0.008 | 0.005 |  | 3.13 | 1.1 |  | 0.008 | 0.005
Exemptions |  |  | NYC 3: DG Info; OASC MAC - NYC 10: Building Types and As-used Adjustment Factors
[6 empty] | Operation Options |  |  |  | Tax |  | Select from List | 0% | 1 | 0% | <-- Informational formula; legacy
| Designated Technology? |  | NYC 4: 1; Westchester 6: Hours; Westchester 8: 5%; OASC MAC - NYC 10: School; OASC MAC - NYC 11: 72%
| TRUE |  | NYC 4: Peak Hours Only; Westchester 6: 11; OASC MAC - NYC 10: Multi-Family Residential; OASC MAC - NYC 11: 74%; OASC MAC - NYC 13: 0%; OASC MAC - NYC 14: <-- Outputs to calculation; equals front page/input value
[6 empty] | 24 Hour Operation |  | 13 |  |  |  | Industrial - Low LF | 65%
| Designated Cutoff Date |  | OASC MAC - NYC 10: Industrial - High LF; OASC MAC - NYC 11: 95%
| 2009-05-31 |  | OASC MAC - NYC 10: Health Care; OASC MAC - NYC 11: 80%
[6 empty] | Location | [5 empty] | Commercial | 70%
| Planning <15% |  | NYC 4: 1; OASC MAC - NYC 10: Alternate formula (would require column of 1, 2, 3 etc. values to left of blg type names)
| FALSE |  | NYC 4: New York City; OASC MAC - NYC 10: VLOOKUP(Q40,N40:P46,3,FALSE)
Westchester County
Has Electric Chilling
TRUE
Phase-In |  |  | NYC 3: Days per Month; OASC MAC - NYC 10: Chiller Offset Percentage
| Phase-In Dates (after) |  | NYC 4: Week; Westchester 5: Wknd/Hol.; Westchester 6: Sum; OASC MAC - NYC 10: 10%; OASC MAC - NYC 11: % of chiller nameplate avail. for cooling
| Start | Stop | NYC 1: + % of SB; NYC 3: Jan; NYC 4: 22; Westchester 5: 9; Westchester 6: 31
| 2004-02-01 | 2008-01-31 | NYC 1: 0%; NYC 3: Feb; NYC 4: 20; Westchester 5: 8; Westchester 6: 28; OASC MAC - NYC 10: 100%; OASC MAC - NYC 11: % of summer peak hours
| 2008-02-01 | 2009-01-31 | NYC 1: 25%; NYC 3: Mar; NYC 4: 22; Westchester 5: 9; Westchester 6: 31
| 2009-02-01 | 2010-01-31 | NYC 1: 50%; NYC 3: Apr; NYC 4: 21; Westchester 5: 9; Westchester 6: 30
| 2010-02-01 | 2011-01-31 | NYC 1: 75%; NYC 3: May; NYC 4: 22; Westchester 5: 9; Westchester 6: 31
| 2011-02-01 |  | NYC 1: 100%; NYC 3: Jun; NYC 4: 21; Westchester 5: 9; Westchester 6: 30; OASC MAC - NYC 10: Price Relationships
[5 empty] | Jul | 22 | 9 | 31 |  |  |  | 115% | On Peak % of Avg.
| Phase-in Cutoff Date |  | NYC 3: Aug; NYC 4: 22; Westchester 5: 9; Westchester 6: 31; OASC MAC - NYC 10: 85%; OASC MAC - NYC 11: Off Peak % of Avg.
| 2011-02-01 |  | NYC 3: Sep; NYC 4: 21; Westchester 5: 9; Westchester 6: 30
[5 empty] | Oct | 22 | 9 | 31 |  |  |  | kWh Volume Relationships
[5 empty] | Nov | 21 | 9 | 30 |  |  |  | 55% | consumption ON-Peak
[5 empty] | Dec | 22 | 9 | 31
365
Note on AG3: Tariff gives these rates in Cents/kWh; this section changes the rates to $/kWh.
Note on B5: Output of rate class input selection box on "Inputs" sheet. Data located:
Note on F5: 8 - 6
Note on G5: 8 - 10
Note on AA5: M-F, 8am - 6pm
Note on AO5: Rates II and III charge for kWh both on-peak and "all other" (same as off-peak, but this uses "all other" for consistency)
Note on J6: Not Used - Holdover from earlier draft but not deleted b/c of column numbering in Row 1.
Note on O6: 1st 100 kW
Note on P6: next 800 kW (up to 900)
Note on Q6: Next 1100 kW (up to 2000)
Note on R6: Over 2,000 kW
Note on Z6: Over 2,000 kW
Note on AL6: Over 800,000 kWh
Note on B8: Rate III set to = Rate I; tariff indicates SC-4 rates for "not subject to Rate II"
Note on O8: Rate III - Time of Use
Note on X9: Over 100 kW
Note on B11: Rate III set to = Rate I; tariff indicates SC-4 rates for "not subject to Rate II"
Note on O11: Rate III - Time of Use
Note on X12: Over 900 kW
Note on AL12: Over 15,000 kWh
Note on B14: Rate III set to = Rate I; tariff indicates SC-4 rates for "not subject to Rate II"
Note on O14: Rate III - Time of Use
Note on C15: Customers on SC-12 energy only rates are not assessed here; Customers who take service under SC-12 NON-demand rates are NOT subject to standby. A limited number of residential customers are in this rare situation.
Note on B24: Indirect output of rate class selection on "Inputs" sheet--copied from main rate output above Data located:
Note on F24: AU1 = As-Used Demand, Period 1, and AU@=As-Used Demand Period 2
Note on D25: Dummy Data
Note on O40: cyoung: Output from Input "Building Type" selection.
Note on P40: cyoung: Info only output based on Building Type selection (input); not used in calculation, to allow user override from Inputs (which changes cell below). It could be activated to prevent user override of the Input, but that is not recommended.
Note on G41: Output of "Planned Operation" (D29) on Inputs & Outputs sheet
Note on K41: Output not yet assigned
Note on P42: Simply equals front page, so user may override input there.
Note on B45: Set in SC-14 RA Tariff Leaf 142
Note on G47: CSY: Set by "Location" input selection
Note on G52: CSY: Set by "chiller" checkbox
Note on M55: Assumed Chiller Demand Offset possible from thermal recovery (% off of genset nameplate). Can set spreadsheet operation here.
Note on M57: Assumed Chiller operates during __% of summer peak hours Can set spreadsheet operation here.
Note on M61: CSY: If only average commodity prices are know, this inflates on-peak and deflates off-peak consumption. Can set spreadsheet operation here. (Rate I customers pay the same MSC all hours, so set these to 100%.)
Note on B64: Set in SC-14 RA Tariff Leaf ___
Note on M65: CSY: If only total kWh consumption is know, this sets the % used on-peak, and leaves the rest as off-peak consumption. Can set spreadsheet operation here. 100% means that off-peak consumption or prices are not relevant.
Note on I68: Checks Sum of days

## CHP & Energy
| CHP Operation |  | Selection: 11 hours | [7 empty] | Hours of Operation | [6 empty] | Nameplate: 300 |  | CHP Production
| CHP Operating Hours | [5 empty] | Days per Month |  |  |  | Weekday Hours |  | Off Peak Hours |  |  |  |  | kW Net Output |  | CHP kWh per Month
|  | Operation | On Peak | On Peak 2 | Off Peak | Blend | Week | Wknd/Hol. | Sum |  | On Peak | On Peak 2 | Off Peak | Wknd+Holiday | Tot. Off | Blend | Parasitic | (less parasitics) |  | On Peak | P2 | Off Hours | Off Days | Tot.Off kWh | All Hrs
| January | Peak | 11 |  | 0 | 11 | 22 | 0 | 31 |  | 242 | 0 | 0 | 0 | 0 | 242 | 5% | 285 |  | 68970 | 68970 | 0 | 0 | 0 | 68970
| February | Peak | 11 |  | 0 | 11 | 20 | 0 | 28 |  | 220 | 0 | 0 | 0 | 0 | 220 | 5% | 285 |  | 62700 | 62700 | 0 | 0 | 0 | 62700
| March | Peak | 11 |  | 0 | 11 | 22 | 0 | 31 |  | 242 | 0 | 0 | 0 | 0 | 242 | 5% | 285 |  | 68970 | 68970 | 0 | 0 | 0 | 68970
| April | Peak | 11 |  | 0 | 11 | 21 | 0 | 30 |  | 231 | 0 | 0 | 0 | 0 | 231 | 5% | 285 |  | 65835 | 65835 | 0 | 0 | 0 | 65835
| May | Peak | 11 |  | 0 | 11 | 22 | 0 | 31 |  | 242 | 0 | 0 | 0 | 0 | 242 | 5% | 285 |  | 68970 | 68970 | 0 | 0 | 0 | 68970
| June | Peak | 11 |  | 0 | 11 | 21 | 0 | 30 |  | 231 | 0 | 0 | 0 | 0 | 231 | 5% | 285 |  | 65835 | 65835 | 0 | 0 | 0 | 65835
| July | Peak | 11 |  | 0 | 11 | 22 | 0 | 31 |  | 242 | 0 | 0 | 0 | 0 | 242 | 5% | 285 |  | 68970 | 68970 | 0 | 0 | 0 | 68970
| August | Peak | 11 |  | 0 | 11 | 22 | 0 | 31 |  | 242 | 0 | 0 | 0 | 0 | 242 | 5% | 285 |  | 68970 | 68970 | 0 | 0 | 0 | 68970
| September | Peak | 11 |  | 0 | 11 | 21 | 0 | 30 |  | 231 | 0 | 0 | 0 | 0 | 231 | 5% | 285 |  | 65835 | 65835 | 0 | 0 | 0 | 65835
| October | Peak | 11 |  | 0 | 11 | 22 | 0 | 31 |  | 242 | 0 | 0 | 0 | 0 | 242 | 5% | 285 |  | 68970 | 68970 | 0 | 0 | 0 | 68970
| November | Peak | 11 |  | 0 | 11 | 21 | 0 | 30 |  | 231 | 0 | 0 | 0 | 0 | 231 | 5% | 285 |  | 65835 | 65835 | 0 | 0 | 0 | 65835
| December | Peak | 11 |  | 0 | 11 | 22 | 0 | 31 |  | 242 | 0 | 0 | 0 | 0 | 242 | 5% | 285 |  | 68970 | 68970 | 0 | 0 | 0 | 68970
[12 empty] | Hours: | 0 | 0 |  | 2838
| Monthly kWh Purchases | [15 empty] | Electric Chiller Offsets: kW Demand and kWh Energy
| From Utility (Inputs & Outputs (kWh)) | [5 empty] | Modified Consumption for Calculations |  |  |  |  | Minus kWh CHP Production | [6 empty] | kWh Offset
|  |  | On Peak 1 | On Peak 2 | Off Peak | Blend | On Peak 1 | On Peak 2 | Off Peak | Blend/All |  | On Peak 1 | On Peak 2 | Off Peak | Blend |  | kW Offset |  | Run Hours | On Peak | Off Hours | Off Days | Tot. Off | All Hrs
W | January |  | 85000 |  | 67000 | 152000 | 85000 |  | 67000 | 152000 |  | 16030 | 0 | 67000 | 83030 |  |  |  | 242 | 0 |  |  | 0 | 0
W | February |  | 85000 |  | 67000 | 152000 | 85000 |  | 67000 | 152000 |  | 22300 | 0 | 67000 | 89300 |  |  |  | 220 | 0 |  |  | 0 | 0
W | March |  | 85000 |  | 67000 | 152000 | 85000 |  | 67000 | 152000 |  | 16030 | 0 | 67000 | 83030 |  |  |  | 242 | 0 |  |  | 0 | 0
W | April |  | 144000 |  | 50000 | 194000 | 144000 |  | 50000 | 194000 |  | 78165 | 0 | 50000 | 128165 |  |  |  | 231 | 0 |  |  | 0 | 0
W | May |  | 108000 |  | 50000 | 158000 | 108000 |  | 50000 | 158000 |  | 39030 | 0 | 50000 | 89030 |  | 30 |  | 242 | 7260 |  |  | 0 | 7260
S | June |  | 108000 |  | 50000 | 158000 | 108000 |  | 50000 | 158000 |  | 42165 | 0 | 50000 | 92165 |  | 30 |  | 231 | 6930 |  |  | 0 | 6930
S | July |  | 108000 |  | 50000 | 158000 | 108000 |  | 50000 | 158000 |  | 39030 | 0 | 50000 | 89030 |  | 30 |  | 242 | 7260 |  |  | 0 | 7260
S | August |  | 108000 |  | 50000 | 158000 | 108000 |  | 50000 | 158000 |  | 39030 | 0 | 50000 | 89030 |  | 30 |  | 242 | 7260 |  |  | 0 | 7260
S | September |  | 108000 |  | 50000 | 158000 | 108000 |  | 50000 | 158000 |  | 42165 | 0 | 50000 | 92165 |  | 30 |  | 231 | 6930 |  |  | 0 | 6930
W | October |  | 85000 |  | 48000 | 133000 | 85000 |  | 48000 | 133000 |  | 16030 | 0 | 48000 | 64030 |  |  |  | 242 | 0 |  |  | 0 | 0
W | November |  | 85000 |  | 67000 | 152000 | 85000 |  | 67000 | 152000 |  | 19165 | 0 | 67000 | 86165 |  |  |  | 231 | 0 |  |  | 0 | 0
W | December |  | 85000 |  | 67000 | 152000 | 85000 |  | 67000 | 152000 |  | 16030 | 0 | 67000 | 83030 |  |  |  | 242 | 0 |  |  | 0 | 0
[7 empty] | 55% | On-Peak kWh consumption | [14 empty] | An. Addl. kWh Saved | 35640
Commodity Costs (kWh)
|  | Energy Prices ($/kWh) |  |  | Modified for Use |  | Monthly Energy $$$ w/o CHP |  |  |  |  | Monthly Energy $$$ with CHP | [6 empty] | Monthly Energy $ SAVED with CHP and Chiller
|  |  | On Peak | Off Peak | On Peak | Off Peak | On Peak 1 | On Peak 2 | Off Peak | Blend |  | On Peak 1 | On Peak 2 | Off Peak | Blend |  |  |  |  | On Peak 1 | On Peak 2 |  | Off Peak | Blend
| January |  | 0.12 | 0.08 | 0.12 | 0.08 | 10200 |  | 5360 |  |  | 1923.6 |  | 5360 | [5 empty] | 0 |  |  | 0
| February |  | 0.12 | 0.08 | 0.12 | 0.08 | 10200 |  | 5360 |  |  | 2676 |  | 5360 | [5 empty] | 0 |  |  | 0
| March |  | 0.11 | 0.09 | 0.11 | 0.09 | 9350 |  | 6030 |  |  | 1763.3 |  | 6030 | [5 empty] | 0 |  |  | 0
| April |  | 0.1 | 0.08 | 0.1 | 0.08 | 14400 |  | 4000 |  |  | 7816.5 |  | 4000 | [5 empty] | 0 |  |  | 0
| May |  | 0.11 | 0.07 | 0.11 | 0.07 | 11880 |  | 3500 |  |  | 4293.3 |  | 3500 | [5 empty] | 798.6 |  |  | 0
| June |  | 0.12 | 0.07 | 0.12 | 0.07 | 12960 |  | 3500 |  |  | 5059.8 |  | 3500 | [5 empty] | 831.6 |  |  | 0
| July |  | 0.13 | 0.09 | 0.13 | 0.09 | 14040 |  | 4500 |  |  | 5073.9 |  | 4500 | [5 empty] | 943.8 |  |  | 0
| August |  | 0.14 | 0.09 | 0.14 | 0.09 | 15120 |  | 4500 |  |  | 5464.2 |  | 4500 | [5 empty] | 1016.4 |  |  | 0
| September |  | 0.11 | 0.08 | 0.11 | 0.08 | 11880 |  | 4000 |  |  | 4638.15 |  | 4000 | [5 empty] | 762.3 |  |  | 0
| October |  | 0.11 | 0.08 | 0.11 | 0.08 | 9350 |  | 3840 |  |  | 1763.3 |  | 3840 | [5 empty] | 0 |  |  | 0
| November |  | 0.12 | 0.1 | 0.12 | 0.1 | 10200 |  | 6700 |  |  | 2299.8 |  | 6700 | [5 empty] | 0 |  |  | 0
| December |  | 0.12 | 0.1 | 0.12 | 0.1 | 10200 |  | 6700 |  |  | 1923.6 |  | 6700 | [5 empty] | 0 |  |  | 0
[5 empty] | 115% | 85% | 139780 |  | 57990 |  |  | 44695.45 |  | 57990 | [5 empty] | 4352.7 |  |  | 0
[10 empty] | 197770 |  |  |  |  | 102685.45 | [8 empty] | 4352.7
Compute Load Factor
|  | w/o CHP | w/ CHP
| January | 43.47% | 5.027%
| February | 48.13% | 5.986%
| March | 43.47% | 5.027%
| April | 58.57% | 8.477%
| May | 42.47% | 4.638%
| June | 43.8% | 4.939%
| July | 21.22% | 1.393%
| August | 42.47% | 4.638%
| September | 43.89% | 4.962%
| October | 38.86% | 4.098%
| November | 44.92% | 5.391%
| December | 43.47% | 5.027%
| Average | 42.89% | 4.967%
Note on D1: CSY: Info on Input selection.
Note on I2: Data in "Tables" sheet
Note on U2: Did not name this value, to maintain user ability input different discounts per month if desired (i.e. microturbines in summer)
Note on E3: Not Yet Used: Peak days 8am - 10pm ** While this is blank some cells in OASC calculation (properly) remain zero**
Note on N3: Not Yet Used: Peak days 8am - 10pm
Note on X3: Placeholder: This simply equals the "on peak" production.
Note on F4: Sets to zero if "on peak" operation is selected
Note on J4: Sets to zero if "on peak" operation is selected
Note on T18: Discount summer peak demand and energy use by % off genset nameplate (summer months)
Note on I19: B/c users may not know on v. off peak kWh consumption, this makes assumption: if only "peak" is entered, this splits consumption between on- and off-peak per a ratio set in Tables & reported below. Note the "blend" figure to left in Col. G is still used in calculations, but should always equal the Blend/All figures here in Col. K.
Note on N19: This shows kWh drawn from grid, after net CHP energy production.
Note on V19: Can't be greater than (consumption - CHP production); (can't offset more chilling demand than kWh would be purchased).
Note on D20: Direct copy from Inputs & Outputs page
Note on E20: Not Yet Used: requires input addition. Peak days 8am - 10pm
Note on I20: cyst: Using conditional formatting these turn bold if no off-peak consumption is input.
Note on J20: Not Yet Used: Peak days 8am - 10pm
Note on N20: No Net Metering: if CHP production exceeds site load, kWh sets to zero.
Note on O20: Not Yet Used: Peak days 8am - 10pm
Note on T20: Nameplate * x%
Note on V20: Tool assumes that the chiller runs __% of the month's peak hours.
Note on W20: kW * Hours (Max of current usage w/ CHP & chiller potential; can offset UP TO post- CHP consumption, value is subtracted later)
Note on X21: This COULD subtract chiller kWh for all hours (kW x off hours) but currently assumes chiller only runs on peak.
Note on F36: B/c users may not know on v. off peak prices, this if only "peak" prices are input, this assumes the price is average and then increases the peak and reduces the off peak prices by the factors set in Tables and displayed in pink below. To disable, change both factors to 100% in Tables sheet.
Note on D37: This block simply mirrors the user commodity price input.
Note on J37: Not Yet Used: Peak days 8am - 10pm
Note on O37: Not Yet Used: Peak days 8am - 10pm
Note on X37: Not Yet Used: Peak days 8am - 10pm
Note on AA51: CSY: Unlike other totals, this is not an amount to pay, but the amount steam chilling saves.
Note on B55: CSY: Actual Consumption / (monthly peak*total hours)

## OASC
OASC Demand
|  | OASC Demand Rates ($/kW) | [14 empty] | OASC Volumetric Delivery ($/kWh) | [8 empty] | OASC MAC | [5 empty] | SBC and Tax
|  | Summer |  |  |  | Winter |  |  |  | Summer |  |  | Winter |  |  |  | Summer |  | Winter |  | Summer |  |  | Winter |  | MAC Rates | [5 empty] | Rates - All Classes
| OASC RATES | Block 1 | Block 2 | Block 3 | Block 4 | Block 1 | Block 2 | Block 3 | Block 4 | Period 1 | Period 2 | All | Period 1 | Period 2 | All |  | Block 1 | Block 2 | Block 1 | Block 2 | Period 1 | Period 2 | All Other | Period 2 | All Other | kW - P1 | kW - P2 | kW - All | kWh-Pk | kWh-Off | kWh-All | SBC | RPS | Tax - NY | Tax - West
| apply rate from column: | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 24 | 25 | 26 | 27 | 28 | 29 |  | 30 | 31 | 32 | 33 | 36 | 37 | 38 | 39 | 40 | 9 | 10 | 11 | 12 | 13 | 14 | 43 | 44 | 45 | 46
W | January | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.86 | 11.09 | 10.94 | 0 | 8.14 | 3.54 |  | 0 | 0 | 0 | 0 | 0 | 0.0058 | 0.0058 | 0.0058 | 0.0058 |  | 1.5 | 0 | 0.008 | 0.005 | 0 | 0.0017 | 0.0006 | NO TAXES IN THIS ESTIMATE
W | February | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.86 | 11.09 | 10.94 | 0 | 8.14 | 3.54 |  | 0 | 0 | 0 | 0 | 0 | 0.0058 | 0.0058 | 0.0058 | 0.0058 |  | 1.5 | 0 | 0.008 | 0.005 | 0 | 0.0017 | 0.0006
W | March | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.86 | 11.09 | 10.94 | 0 | 8.14 | 3.54 |  | 0 | 0 | 0 | 0 | 0 | 0.0058 | 0.0058 | 0.0058 | 0.0058 |  | 1.5 | 0 | 0.008 | 0.005 | 0 | 0.0017 | 0.0006
W | April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.86 | 11.09 | 10.94 | 0 | 8.14 | 3.54 |  | 0 | 0 | 0 | 0 | 0 | 0.0058 | 0.0058 | 0.0058 | 0.0058 |  | 1.5 | 0 | 0.008 | 0.005 | 0 | 0.0017 | 0.0006
W | May | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.86 | 11.09 | 10.94 | 0 | 8.14 | 3.54 |  | 0 | 0 | 0 | 0 | 0 | 0.0058 | 0.0058 | 0.0058 | 0.0058 |  | 1.5 | 0 | 0.008 | 0.005 | 0 | 0.0017 | 0.0006
S | June | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.86 | 11.09 | 10.94 | 0 | 8.14 | 3.54 |  | 0 | 0 | 0 | 0 | 0 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 1.23 | 1.5 | 0 | 0.008 | 0.005 | 0 | 0.0017 | 0.0006
S | July | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.86 | 11.09 | 10.94 | 0 | 8.14 | 3.54 |  | 0 | 0 | 0 | 0 | 0 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 1.23 | 1.5 | 0 | 0.008 | 0.005 | 0 | 0.0017 | 0.0006
S | August | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.86 | 11.09 | 10.94 | 0 | 8.14 | 3.54 |  | 0 | 0 | 0 | 0 | 0 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 1.23 | 1.5 | 0 | 0.008 | 0.005 | 0 | 0.0017 | 0.0006
S | September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.86 | 11.09 | 10.94 | 0 | 8.14 | 3.54 |  | 0 | 0 | 0 | 0 | 0 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 1.23 | 1.5 | 0 | 0.008 | 0.005 | 0 | 0.0017 | 0.0006
W | October | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.86 | 11.09 | 10.94 | 0 | 8.14 | 3.54 |  | 0 | 0 | 0 | 0 | 0 | 0.0058 | 0.0058 | 0.0058 | 0.0058 |  | 1.5 | 0 | 0.008 | 0.005 | 0 | 0.0017 | 0.0006
W | November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.86 | 11.09 | 10.94 | 0 | 8.14 | 3.54 |  | 0 | 0 | 0 | 0 | 0 | 0.0058 | 0.0058 | 0.0058 | 0.0058 |  | 1.5 | 0 | 0.008 | 0.005 | 0 | 0.0017 | 0.0006
W | December | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.86 | 11.09 | 10.94 | 0 | 8.14 | 3.54 |  | 0 | 0 | 0 | 0 | 0 | 0.0058 | 0.0058 | 0.0058 | 0.0058 |  | 1.5 | 0 | 0.008 | 0.005 | 0 | 0.0017 | 0.0006
| QUANTITIES: Demand Drawn | [15 empty] | QUANTITIES: Energy Drawn | [8 empty] | Quantities Drawn - MAC |  |  | IS THIS TOO MUCH KWH??? |  |  | kWh Quantities - SBC/RPS
W | January | 16: 470; 17: 470; 18: 470; 19: 470; 27: 470; 28: 470; 29: 470 |  | 152000 | 152000 | 152000 | 152000 | 85000 | 0 | 67000 | 0 | 67000 | 470 | 470 | 470 | 85000 | 67000 | 152000 | 152000 | 152000
W | February | 16: 470; 17: 470; 18: 470; 19: 470; 27: 470; 28: 470; 29: 470 |  | 152000 | 152000 | 152000 | 152000 | 85000 | 0 | 67000 | 0 | 67000 | 470 | 470 | 470 | 85000 | 67000 | 152000 | 152000 | 152000
W | March | 16: 470; 17: 470; 18: 470; 19: 470; 27: 470; 28: 470; 29: 470 |  | 152000 | 152000 | 152000 | 152000 | 85000 | 0 | 67000 | 0 | 67000 | 470 | 470 | 470 | 85000 | 67000 | 152000 | 152000 | 152000
W | April | 16: 460; 17: 460; 18: 460; 19: 460; 27: 460; 28: 460; 29: 460 |  | 194000 | 194000 | 194000 | 194000 | 144000 | 0 | 50000 | 0 | 50000 | 460 | 460 | 460 | 144000 | 50000 | 194000 | 194000 | 194000
W | May | 16: 500; 17: 500; 18: 500; 19: 500; 27: 500; 28: 500; 29: 500 |  | 158000 | 158000 | 158000 | 158000 | 108000 | 0 | 50000 | 0 | 50000 | 500 | 500 | 500 | 108000 | 50000 | 158000 | 158000 | 158000
S | June | 12: 501; 13: 501; 14: 501; 15: 501; 24: 501; 25: 501; 26: 501 |  | 158000 | 158000 | 158000 | 158000 | 108000 | 0 | 50000 | 0 | 50000 | 501 | 501 | 501 | 108000 | 50000 | 158000 | 158000 | 158000
S | July | 12: 1001; 13: 1001; 14: 1001; 15: 1001; 24: 1001; 25: 1001; 26: 1001 |  | 158000 | 158000 | 158000 | 158000 | 108000 | 0 | 50000 | 0 | 50000 | 1001 | 1001 | 1001 | 108000 | 50000 | 158000 | 158000 | 158000
S | August | 12: 500; 13: 500; 14: 500; 15: 500; 24: 500; 25: 500; 26: 500 |  | 158000 | 158000 | 158000 | 158000 | 108000 | 0 | 50000 | 0 | 50000 | 500 | 500 | 500 | 108000 | 50000 | 158000 | 158000 | 158000
S | September | 12: 500; 13: 500; 14: 500; 15: 500; 24: 500; 25: 500; 26: 500 |  | 158000 | 158000 | 158000 | 158000 | 108000 | 0 | 50000 | 0 | 50000 | 500 | 500 | 500 | 108000 | 50000 | 158000 | 158000 | 158000
W | October | 16: 460; 17: 460; 18: 460; 19: 460; 27: 460; 28: 460; 29: 460 |  | 133000 | 133000 | 133000 | 133000 | 85000 | 0 | 48000 | 0 | 48000 | 460 | 460 | 460 | 85000 | 48000 | 133000 | 133000 | 133000
W | November | 16: 470; 17: 470; 18: 470; 19: 470; 27: 470; 28: 470; 29: 470 |  | 152000 | 152000 | 152000 | 152000 | 85000 | 0 | 67000 | 0 | 67000 | 470 | 470 | 470 | 85000 | 67000 | 152000 | 152000 | 152000
W | December | 16: 470; 17: 470; 18: 470; 19: 470; 27: 470; 28: 470; 29: 470 |  | 152000 | 152000 | 152000 | 152000 | 85000 | 0 | 67000 | 0 | 67000 | 470 | 470 | 470 | 85000 | 67000 | 152000 | 152000 | 152000
Selected: | SC-9_Rate_II | [14 empty] | Selected: | SC-9_Rate_II
| QUANTITIES 2 - Hours / Blocks | 24: Demand Time Blocks |  | Volume Blocks 1 |  |  |  | Energy Time Periods |  |  |  |  | Time Periods for MAC
| "Block Column" | 20 | 21 | 22 | 23 | 20 | 21 | 22 | 23 | [7 empty] | 34 | 35 | 34 | 35
| "Block Size" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0 | 0 | 0 | 0 | (Below entered "as is" b/c assumption of "on peak") |  |  |  |  | (Blocks unnecessary for MAC; use Energy Time Periods section at left)
| January | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 470 | 470 |  | 0 | 0 | 0 | 0 | 85000 | 0 | 152000 | 0 | 152000
| February | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 470 | 470 |  | 0 | 0 | 0 | 0 | 85000 | 0 | 152000 | 0 | 152000
| March | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 470 | 470 |  | 0 | 0 | 0 | 0 | 85000 | 0 | 152000 | 0 | 152000
| April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 460 | 460 |  | 0 | 0 | 0 | 0 | 144000 | 0 | 194000 | 0 | 194000
| May | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 500 | 500 |  | 0 | 0 | 0 | 0 | 108000 | 0 | 158000 | 0 | 158000
| June | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 501 | 501 | 501 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 108000 | 0 | 158000 | 0 | 158000
| July | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1001 | 1001 | 1001 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 108000 | 0 | 158000 | 0 | 158000
| August | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 500 | 500 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 108000 | 0 | 158000 | 0 | 158000
| September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 500 | 500 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 108000 | 0 | 158000 | 0 | 158000
| October | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 460 | 460 |  | 0 | 0 | 0 | 0 | 85000 | 0 | 133000 | 0 | 133000
| November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 470 | 470 |  | 0 | 0 | 0 | 0 | 85000 | 0 | 152000 | 0 | 152000
| December | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 470 | 470 |  | 0 | 0 | 0 | 0 | 85000 | 0 | 152000 | 0 | 152000
| Calculation 1 - Original Demand x Rates | [8 empty] | Demand x Rates | [6 empty] | Volume x Rates | [8 empty] | MAC Quantities x Rates (w/o CHP) | [5 empty] | SBC/RPS Quantities x Rates (w/o CHP)
| January | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3825.8 | 1663.8 |  | 0 | 0 | 0 | 0 | 0 | 0 | 881.6 | 0 | 881.6 | 0 | 705 | 0 | 680 | 335 | 0 | 258.4 | 91.2
| February | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3825.8 | 1663.8 |  | 0 | 0 | 0 | 0 | 0 | 0 | 881.6 | 0 | 881.6 | 0 | 705 | 0 | 680 | 335 | 0 | 258.4 | 91.2
| March | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3825.8 | 1663.8 |  | 0 | 0 | 0 | 0 | 0 | 0 | 881.6 | 0 | 881.6 | 0 | 705 | 0 | 680 | 335 | 0 | 258.4 | 91.2
| April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3744.4 | 1628.4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1125.2 | 0 | 1125.2 | 0 | 690 | 0 | 1152 | 250 | 0 | 329.8 | 116.4
| May | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4070 | 1770 |  | 0 | 0 | 0 | 0 | 0 | 0 | 916.4 | 0 | 916.4 | 0 | 750 | 0 | 864 | 250 | 0 | 268.6 | 94.8
| June | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2935.86 | 5556.09 | 5480.94 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 916.4 | 0 | 916.4 | 616.23 | 751.5 | 0 | 864 | 250 | 0 | 268.6 | 94.8
| July | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5865.86 | 11101.09 | 10950.94 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 916.4 | 0 | 916.4 | 1231.23 | 1501.5 | 0 | 864 | 250 | 0 | 268.6 | 94.8
| August | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2930 | 5545 | 5470 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 916.4 | 0 | 916.4 | 615 | 750 | 0 | 864 | 250 | 0 | 268.6 | 94.8
| September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2930 | 5545 | 5470 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 916.4 | 0 | 916.4 | 615 | 750 | 0 | 864 | 250 | 0 | 268.6 | 94.8
| October | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3744.4 | 1628.4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 771.4 | 0 | 771.4 | 0 | 690 | 0 | 680 | 240 | 0 | 226.1 | 79.8
| November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3825.8 | 1663.8 |  | 0 | 0 | 0 | 0 | 0 | 0 | 881.6 | 0 | 881.6 | 0 | 705 | 0 | 680 | 335 | 0 | 258.4 | 91.2
| December | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3825.8 | 1663.8 |  | 0 | 0 | 0 | 0 | 0 | 0 | 881.6 | 0 | 881.6 | 0 | 705 | 0 | 680 | 335 | 0 | 258.4 | 91.2
| Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14661.72 | 27747.18 | 27371.88 | 0 | 30687.8 | 13345.8 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10886.6 | 0 | 10886.6 | 3077.46 | 9408 | 0 | 9552 | 3415 | 0 | 3190.9 | 1126.2
[29 empty] | MAC w/o CHP |  | 25452.46 | w/o CHP | 4317.1
| QUANTITIES 3 - Subtract CHP Capacity (Net Output) for New Demand w/ CHP | [15 empty] | Subtract CHP Production (All Hours from CHP&E Sheet) [Not yet in blocks] | [8 empty] | Subtract CHP Capacity (net, from left) | [5 empty] | SBC/RPS Quantities (Subtract CHP Production)
| January | 20: 185; 21: 185; 22: 185; 23: 185 |  |  |  | 185 | 185 | 185 |  |  |  | 83030 | 83030 |  |  |  | 0 | 67000 | 185 | 185 | 185 | 0 | 67000 | 83030 | 83030 | 83030
| February | 20: 185; 21: 185; 22: 185; 23: 185 |  |  |  | 185 | 185 | 185 |  |  |  | 89300 | 89300 |  |  |  | 0 | 67000 | 185 | 185 | 185 | 0 | 67000 | 89300 | 89300 | 89300
| March | 20: 185; 21: 185; 22: 185; 23: 185 |  |  |  | 185 | 185 | 185 |  |  |  | 83030 | 83030 |  |  |  | 0 | 67000 | 185 | 185 | 185 | 0 | 67000 | 83030 | 83030 | 83030
| April | 20: 175; 21: 175; 22: 175; 23: 175 |  |  |  | 175 | 175 | 175 |  |  |  | 128165 | 128165 |  |  |  | 0 | 50000 | 175 | 175 | 175 | 0 | 50000 | 128165 | 128165 | 128165
| May | 20: 215; 21: 215; 22: 215; 23: 215 |  |  |  | 215 | 215 | 215 |  |  |  | 89030 | 89030 |  |  |  | 0 | 50000 | 215 | 215 | 215 | 0 | 50000 | 89030 | 89030 | 89030
| June | 20: 216; 21: 216; 22: 216; 23: 216 | 216 | 216 | 216 |  |  |  |  | 92165 | 92165 |  |  | 42165 | 0 | 50000 |  |  | 216 | 216 | 216 | 0 | 50000 | 92165 | 92165 | 92165
| July | 20: 716; 21: 716; 22: 716; 23: 716 | 716 | 716 | 716 |  |  |  |  | 89030 | 89030 |  |  | 39030 | 0 | 50000 |  |  | 716 | 716 | 716 | 0 | 50000 | 89030 | 89030 | 89030
| August | 20: 215; 21: 215; 22: 215; 23: 215 | 215 | 215 | 215 |  |  |  |  | 89030 | 89030 |  |  | 39030 | 0 | 50000 |  |  | 215 | 215 | 215 | 0 | 50000 | 89030 | 89030 | 89030
| September | 20: 215; 21: 215; 22: 215; 23: 215 | 215 | 215 | 215 |  |  |  |  | 92165 | 92165 |  |  | 42165 | 0 | 50000 |  |  | 0 | 0 | 0 | 0 | 50000 | 92165 | 92165 | 92165
| October | 20: 175; 21: 175; 22: 175; 23: 175 |  |  |  | 175 | 175 | 175 |  |  |  | 64030 | 64030 |  |  |  | 0 | 48000 | 175 | 175 | 175 | 0 | 48000 | 64030 | 64030 | 64030
| November | 20: 185; 21: 185; 22: 185; 23: 185 |  |  |  | 185 | 185 | 185 |  |  |  | 86165 | 86165 |  |  |  | 0 | 67000 | 185 | 185 | 185 | 0 | 67000 | 86165 | 86165 | 86165
| December | 20: 185; 21: 185; 22: 185; 23: 185 |  |  |  | 185 | 185 | 185 |  |  |  | 83030 | 83030 |  |  |  | 0 | 67000 | 185 | 185 | 185 | 0 | 67000 | 83030 | 83030 | 83030
Sets value to Min Production if production exceeds consumption
| QUANTITIES 4 - Hours / Blocks w/ CHP subtracted | [8 empty] | Demand Time Blocks: --CHP | [6 empty] | Volume Blocks 2 |  |  |  | Energy Time Periods |  |  |  |  | Volume Blocks 2 - not used in MAC calculation
| January | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 185 | 185 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67000
| February | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 185 | 185 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67000
| March | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 185 | 185 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67000
| April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 175 | 175 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50000
| May | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215 | 215 | 215 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50000
| June | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216 | 216 | 216 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 42165 | 0 | 50000 | 0 | 0
| July | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 716 | 716 | 716 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 39030 | 0 | 50000 | 0 | 0
| August | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215 | 215 | 215 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 39030 | 0 | 50000 | 0 | 0
| September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215 | 215 | 215 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 42165 | 0 | 50000 | 0 | 0
| October | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 175 | 175 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48000
| November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 185 | 185 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67000
| December | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 185 | 185 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67000
| Calculation 2 - New Demand x Rates | [15 empty] | New Volume x Rates | [8 empty] | New MAC Volume x MAC Rates | [5 empty] | SBC&RPS w/ CHP
| January | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1505.9 | 654.9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 388.6 | 0 | 277.5 | 0 | 0 | 335 | 0 | 141.151 | 49.818
| February | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1505.9 | 654.9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 388.6 | 0 | 277.5 | 0 | 0 | 335 | 0 | 151.81 | 53.58
| March | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1505.9 | 654.9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 388.6 | 0 | 277.5 | 0 | 0 | 335 | 0 | 141.151 | 49.818
| April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1424.5 | 619.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 262.5 | 0 | 0 | 250 | 0 | 217.8805 | 76.899
| May | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1750.1 | 761.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 322.5 | 0 | 0 | 250 | 0 | 151.351 | 53.418
| June | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1265.76 | 2395.44 | 2363.04 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 265.68 | 324 | 0 | 0 | 250 | 0 | 156.6805 | 55.299
| July | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4195.76 | 7940.44 | 7833.04 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 880.68 | 1074 | 0 | 0 | 250 | 0 | 151.351 | 53.418
| August | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1259.9 | 2384.35 | 2352.1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 264.45 | 322.5 | 0 | 0 | 250 | 0 | 151.351 | 53.418
| September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1259.9 | 2384.35 | 2352.1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 156.6805 | 55.299
| October | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1424.5 | 619.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278.4 | 0 | 262.5 | 0 | 0 | 240 | 0 | 108.851 | 38.418
| November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1505.9 | 654.9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 388.6 | 0 | 277.5 | 0 | 0 | 335 | 0 | 146.4805 | 51.699
| December | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1505.9 | 654.9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 388.6 | 0 | 277.5 | 0 | 0 | 335 | 0 | 141.151 | 49.818
| Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7981.32 | 15104.58 | 14900.28 | 0 | 12128.6 | 5274.6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1160 | 0 | 2801.4 | 1410.81 | 3955.5 | 0 | 0 | 3415 | 0 | 1815.889 | 640.902
[14 empty] | w/ CHP | 55389.38 | [8 empty] | w/ CHP | 3961.4 |  |  |  |  | MAC w/ CHP | 8781.31 | w/ CHP | 2456.791
| QUANTITIES 6 - Subtract CHP Capacity and Chiller Offset (Net Output - Chiller Savings) for New Demand 2 w/ CHP | [15 empty] | Subtract CHP Production and Chiller Offset from kWh | [8 empty] | MAC Quantities - Subtract CHP Capacity & Chiller Offset (from left) | [5 empty] | SBC/RPS Quantities (Subtract CHP Production AND Chiller)
| January | 20: 185; 21: 185; 22: 185; 23: 185 |  |  |  | 185 | 185 | 185 |  |  |  | 83030 | 83030 |  |  |  | 0 | 242 | 185 | 185 | 185 | 0 | 67000 | 83030 | 83030 | 83030
| February | 20: 185; 21: 185; 22: 185; 23: 185 |  |  |  | 185 | 185 | 185 |  |  |  | 89300 | 89300 |  |  |  | 0 | 4300 | 185 | 185 | 185 | 0 | 67000 | 89300 | 89300 | 89300
| March | 20: 185; 21: 185; 22: 185; 23: 185 |  |  |  | 185 | 185 | 185 |  |  |  | 83030 | 83030 |  |  |  | 0 | 242 | 185 | 185 | 185 | 0 | 67000 | 83030 | 83030 | 83030
| April | 20: 175; 21: 175; 22: 175; 23: 175 |  |  |  | 175 | 175 | 175 |  |  |  | 128165 | 128165 |  |  |  | 0 | 231 | 175 | 175 | 175 | 0 | 50000 | 128165 | 128165 | 128165
| May | 20: 185; 21: 185; 22: 185; 23: 185 |  |  |  | 185 | 185 | 185 |  |  |  | 81770 | 81770 |  |  |  | 0 | 242 | 185 | 185 | 185 | 0 | 50000 | 81770 | 81770 | 81770
| June | 20: 186; 21: 186; 22: 186; 23: 186 | 186 | 186 | 186 |  |  |  |  | 85235 | 85235 |  |  | 35235 | 0 | 231 |  |  | 186 | 186 | 186 | 0 | 50000 | 85235 | 85235 | 85235
| July | 20: 686; 21: 686; 22: 686; 23: 686 | 686 | 686 | 686 |  |  |  |  | 81770 | 81770 |  |  | 31770 | 0 | 242 |  |  | 686 | 686 | 686 | 0 | 50000 | 81770 | 81770 | 81770
| August | 20: 185; 21: 185; 22: 185; 23: 185 | 185 | 185 | 185 |  |  |  |  | 81770 | 81770 |  |  | 31770 | 0 | 242 |  |  | 185 | 185 | 185 | 0 | 50000 | 81770 | 81770 | 81770
| September | 20: 185; 21: 185; 22: 185; 23: 185 | 185 | 185 | 185 |  |  |  |  | 85235 | 85235 |  |  | 35235 | 0 | 231 |  |  | 0 | 0 | 0 | 0 | 50000 | 85235 | 85235 | 85235
| October | 20: 175; 21: 175; 22: 175; 23: 175 |  |  |  | 175 | 175 | 175 |  |  |  | 64030 | 64030 |  |  |  | 0 | 242 | 175 | 175 | 175 | 0 | 48000 | 64030 | 64030 | 64030
| November | 20: 185; 21: 185; 22: 185; 23: 185 |  |  |  | 185 | 185 | 185 |  |  |  | 86165 | 86165 |  |  |  | 0 | 1165 | 185 | 185 | 185 | 0 | 67000 | 86165 | 86165 | 86165
| December | 20: 185; 21: 185; 22: 185; 23: 185 |  |  |  | 185 | 185 | 185 |  |  |  | 83030 | 83030 |  |  |  | 0 | 242 | 185 | 185 | 185 | 0 | 67000 | 83030 | 83030 | 83030
| QUANTITIES 7 - Hours / Blocks w/ CHP subtracted & Chiller Offset | [15 empty] | Volume Blocks 3 ( - CHP production and chiller offset) | [8 empty] | Volume Blocks 3 - not used in MAC calculation
| January | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 185 | 185 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242
| February | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 185 | 185 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4300
| March | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 185 | 185 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242
| April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 175 | 175 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231
| May | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 185 | 185 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242
| June | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 186 | 186 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 35235 | 0 | 231 | 0 | 0
| July | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 686 | 686 | 686 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 31770 | 0 | 242 | 0 | 0
| August | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 185 | 185 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 31770 | 0 | 242 | 0 | 0
| September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 185 | 185 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 35235 | 0 | 231 | 0 | 0
| October | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 175 | 175 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242
| November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 185 | 185 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1165
| December | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 185 | 185 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242
| Calculation 3 - New Demand incl. Chiller Offset x Rates | [15 empty] | Calc 3 - New Volume x Rates | [8 empty] | Calc 3 - New MAC Volume x MAC Rates | [5 empty] | SBC&RPS w/ CHP & Chiller
| January | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1505.9 | 654.9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4036 | 0 | 277.5 | 0 | 0 | 335 | 0 | 141.151 | 49.818
| February | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1505.9 | 654.9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.94 | 0 | 277.5 | 0 | 0 | 335 | 0 | 151.81 | 53.58
| March | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1505.9 | 654.9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4036 | 0 | 277.5 | 0 | 0 | 335 | 0 | 141.151 | 49.818
| April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1424.5 | 619.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3398 | 0 | 262.5 | 0 | 0 | 250 | 0 | 217.8805 | 76.899
| May | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1505.9 | 654.9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4036 | 0 | 277.5 | 0 | 0 | 250 | 0 | 139.009 | 49.062
| June | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1089.96 | 2062.74 | 2034.84 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1.3398 | 0 | 0 | 228.78 | 279 | 0 | 0 | 250 | 0 | 144.8995 | 51.141
| July | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4019.96 | 7607.74 | 7504.84 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1.4036 | 0 | 0 | 843.78 | 1029 | 0 | 0 | 250 | 0 | 139.009 | 49.062
| August | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1084.1 | 2051.65 | 2023.9 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1.4036 | 0 | 0 | 227.55 | 277.5 | 0 | 0 | 250 | 0 | 139.009 | 49.062
| September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1084.1 | 2051.65 | 2023.9 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1.3398 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 144.8995 | 51.141
| October | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1424.5 | 619.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4036 | 0 | 262.5 | 0 | 0 | 240 | 0 | 108.851 | 38.418
| November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1505.9 | 654.9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.757 | 0 | 277.5 | 0 | 0 | 335 | 0 | 146.4805 | 51.699
| December | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1505.9 | 654.9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4036 | 0 | 277.5 | 0 | 0 | 335 | 0 | 141.151 | 49.818
| Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7278.12 | 13773.78 | 13587.48 | 0 | 11884.4 | 5168.4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 5.4868 | 0 | 40.0548 | 1300.11 | 3775.5 | 0 | 0 | 3415 | 0 | 1755.301 | 619.518
[14 empty] | w/ CHP & Chiller | 51692.18 | [8 empty] | w/ CHP & Chiller | 45.5416 |  |  |  |  | Mac w/ CHP & Chiller | 8490.61 | w/ CHP&Chiller | 2374.819
[15 empty] | 7985.7304 | OASC Delivery Savings w/ Chiller Offset
[15 empty] | 4352.7 | CHP sheet savings
[15 empty] | 12338.4304 | Total OASC savings due to Chiller offset of energy and demand
Note on AB3: Estimate of avg. history; note MAC adjustment is volumetric. Used to differ between NYC and Westchester.
Note on K4: M-F, 8am - 6pm
Note on B5: This Row used by the lookups below -- sends Index to appropriate column in "Rate_Table"
Note on AB6: Period 1 MAC is only collected in summer months.
Note on R20: The rates with kWh blocks (rates I) do not care what times the energy is drawn, so the monthly total is used here.
Note on V20: Period 1: Peak Days 8 am - 6 pm
Note on W20: Summer P-2 has same rates as P-1; and only one is collected in kWh charges. (Actually P-2 is collected, but calculating P-1 gives identical result.)
Note on Y20: Period 1: Peak Days 8 am - 6 pm
Note on Z20: 8 am - 10 pm
Note on AB20: P1 demand is not used in Winter calculation, but because it is listed on the tariff with zero values we include it here.
Note on AF20: Off Peak consumption:
Note on B33: Just for convenience so I know what rate should appear here. -- cy
Note on R33: INFO ONLY - which rate is selected on Inputs sheet.
Note on B35: This Row is for the lookup function -- refers the lookup to appropriate column in Main Interface rates table.
Note on L36: cyoung: We don't ask for Period 1 v. Period 2 demand charges; if we did, this is where the difference would appear.
Note on M36: cyoung: the numbers below will not change (be reduced) by on-peak CHP operation; this rate value is "all hours", while the previous two are peak demand charges.
Note on V37: Period 1: Peak Days 8 am - 6 pm
Note on W37: 8 am - 10 pm
Note on Y37: Period 1: Peak Days 8 am - 6 pm
Note on AB37: No change from section above; those values used in computations below.
Note on AI67: From CHP & Energy Sheet
Note on R68: These columns in kWh blocks (Rates I); so use "all hours" quantities. MAX function sets values to min. draw if production exceeds consumption.
Note on W68: Always zero b/c P2 on CHP&Energy sheet has no value
Note on X68: CY: NEED "OTHER" HOURS! Subtracts to find all net hours consumption, or sets min_run*all hours if net consumption is negative. {Takes the greater of: MinDraw*RunHours OR (Origninal total energy purchase)*(Tot. CHP kWh)}
Note on Z68: (Same formula as X68)
Note on AF68: Net"Off Peak" kWh consumption (after CHP production)
Note on AG68: Total kWh from grid net of CHP production
Note on X69: Takes the greater of: MinDraw*RunHours OR (Origninal total energy purchase)*(Tot. CHP kWh)
Note on B82: Copies "Blocks" formulas, now less CHP output. If CHP capacity is greater than demand, sets value to zero. Keeps MinDraw setting intact in Block 1.
Note on R82: No need to change MinDraw if corrected in block above? {I.e., to (Min_Draw*[hours])}
Note on AI113: From CHP & Energy Sheet
Note on R114: "MAX((Min_Draw*'CHP & Energy'!$R4)" represents the minimum monthly kWh grid consumption.
Note on Y114: Operating Hours Note: This is always zero B/C there are no P2 run hours listed in CHP&Energy sheet.
Note on AF114: Need to determine "Off Peak"!
Note on B127: Copies "Blocks" formulas, now less CHP output. If CHP capacity is greater than demand, sets value to zero. Keeps MinDraw setting intact in Block 1.

## Standby
Standby Demand
|  | Primary SB Rates | [6 empty] | MAC SB Rates
|  |  |  | Days in | Summer |  | Winter
| SB RATES | Cust Chg | CD Chg | Month | As-Use 1 | As-Use 2 | As-Use 1 | As-Use 2 |  | MAC Cust | MAC CD | MAC AU1 | MAC AU2
| apply rate from column: | 1 | 2 |  | 3 | 4 | 5 | 6 |  | 1 | 2 | 3 | 4
W | January | 908.12 | 5.41 |  |  |  | 0 | 0.52 | NYC | 377.1383 | 1.7867 |  | 0.17943
W | February | 908.12 | 5.41 |  |  |  | 0 | 0.52 | NYC | 377.1383 | 1.7867 |  | 0.17943
W | March | 908.12 | 5.41 |  |  |  | 0 | 0.52 | NYC | 377.1383 | 1.7867 |  | 0.17943
W | April | 908.12 | 5.41 |  |  |  | 0 | 0.52 | NYC | 377.1383 | 1.7867 |  | 0.17943 |  |  | As-used high and low cases refer to the main calculations rate levels, to left
W | May | 908.12 | 5.41 |  |  |  | 0 | 0.52 | NYC | 377.1383 | 1.7867 | 0.015783 | 0.17943
S | June | 908.12 | 5.41 |  | 0.3423 | 0.691 |  |  | NYC | 377.1383 | 1.7867 | 0.015783 | 0.17943
S | July | 908.12 | 5.41 |  | 0.3423 | 0.691 |  |  | NYC | 377.1383 | 1.7867 | 0.015783 | 0.17943
S | August | 908.12 | 5.41 |  | 0.3423 | 0.691 |  |  | NYC | 377.1383 | 1.7867 | 0.015783 | 0.17943
S | September | 908.12 | 5.41 |  | 0.3423 | 0.691 |  |  | NYC | 377.1383 | 1.7867 | 0.015783 | 0.17943
W | October | 908.12 | 5.41 |  |  |  | 0 | 0.52 | NYC | 377.1383 | 1.7867 | 0.015783 | 0.17943
W | November | 908.12 | 5.41 |  |  |  | 0 | 0.52 | NYC | 377.1383 | 1.7867 |  | 0.17943
W | December | 908.12 | 5.41 |  |  |  | 0 | 0.52 | NYC | 377.1383 | 1.7867 |  | 0.17943
|  |  |  | Days in | Summer |  | Winter | [6 empty] | As-Used Low Case Quantities | [5 empty] | As-Used High Case Quantities
| QUANTITIES | Cust Chg | CD Chg | Month | As-Use 1 | As-Use 2 | As-Use 1 | As-Use 2 | City | MAC Cust | MAC CD | MAC AU1 | MAC AU2 | As-Use 1 | As-Use 2 | As-Use 1 | As-Use 2 | MAC AU1 | MAC AU2 | As-Use 1 | As-Use 2 | As-Use 1 | As-Use 2 | MAC AU1 | MAC AU2
0% | (Finds units by which to multiply rates AND estimates average as-used demand by discounting monthly peak)
W | January | 1 | 500 |  |  |  | 0 | 0 |  | 1 | 500 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 470 | 470 | 470 | 470
W | February | 1 | 500 |  |  |  | 0 | 0 |  | 1 | 500 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 470 | 470 | 470 | 470
W | March | 1 | 500 |  |  |  | 0 | 0 |  | 1 | 500 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 470 | 470 | 470 | 470
W | April | 1 | 500 |  |  |  | 0 | 0 |  | 1 | 500 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 460 | 460 | 460 | 460
W | May | 1 | 500 |  |  |  | 0 | 0 |  | 1 | 500 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 500 | 500 | 500 | 500
S | June | 1 | 500 |  | 0 | 0 |  |  |  | 1 | 500 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 501 | 501 |  |  | 501 | 501
S | July | 1 | 500 |  | 0 | 0 |  |  |  | 1 | 500 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 1001 | 1001 |  |  | 1001 | 1001
S | August | 1 | 500 |  | 0 | 0 |  |  |  | 1 | 500 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 500 | 500 |  |  | 500 | 500
S | September | 1 | 500 |  | 0 | 0 |  |  |  | 1 | 500 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 500 | 500 |  |  | 500 | 500
W | October | 1 | 500 |  |  |  | 0 | 0 |  | 1 | 500 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 460 | 460 | 460 | 460
W | November | 1 | 500 |  |  |  | 0 | 0 |  | 1 | 500 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 470 | 470 | 470 | 470
W | December | 1 | 500 |  |  |  | 0 | 0 |  | 1 | 500 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 470 | 470 | 470 | 470
=MAX(Min_Draw,IF(('Inputs & Outputs'!$F14-'CHP & Energy'!T4)>0,'Inputs & Outputs'!$F14-'CHP & Energy'!T4,0))
| Subtract Net CHP Capacity | [12 empty] | Subtract CHP Capacity | [5 empty] | High Case currently Ignores This Block b/c definition of "high"
| (Finds the units by which to multiply the rates -- accounting for CHP operation, parastics, and min-draw requirement) | [12 empty] | (Low Case: ___) | [5 empty] | (High Case: NOT subtracting CHP capacity)
| January | 1 | 500 |  |  |  | 1 | 1 |  | 1 | 500 | 1 | 1 |  |  | 0 | 0 | 0 | 0 |  |  | 185 | 185 | 470 | 470
| February | 1 | 500 |  |  |  | 1 | 1 |  | 1 | 500 | 1 | 1 |  |  | 0 | 0 | 0 | 0 |  |  | 185 | 185 | 470 | 470
| March | 1 | 500 |  |  |  | 1 | 1 |  | 1 | 500 | 1 | 1 |  |  | 0 | 0 | 0 | 0 |  |  | 185 | 185 | 470 | 470
| April | 1 | 500 |  |  |  | 1 | 1 |  | 1 | 500 | 1 | 1 |  |  | 0 | 0 | 0 | 0 |  |  | 175 | 175 | 460 | 460
| May | 1 | 500 |  |  |  | 1 | 1 |  | 1 | 500 | 1 | 1 |  |  | 0 | 0 | 0 | 0 |  |  | 215 | 215 | 500 | 500
| June | 1 | 500 |  | 1 | 1 |  |  |  | 1 | 500 | 1 | 1 | 0 | 0 |  |  | 0 | 0 | 216 | 216 |  |  | 501 | 501
| July | 1 | 500 |  | 1 | 1 |  |  |  | 1 | 500 | 1 | 1 | 0 | 0 |  |  | 0 | 0 | 716 | 716 |  |  | 1001 | 1001
| August | 1 | 500 |  | 1 | 1 |  |  |  | 1 | 500 | 1 | 1 | 0 | 0 |  |  | 0 | 0 | 215 | 215 |  |  | 500 | 500
| September | 1 | 500 |  | 1 | 1 |  |  |  | 1 | 500 | 1 | 1 | 0 | 0 |  |  | 0 | 0 | 215 | 215 |  |  | 500 | 500
| October | 1 | 500 |  |  |  | 1 | 1 |  | 1 | 500 | 1 | 1 |  |  | 0 | 0 | 0 | 0 |  |  | 175 | 175 | 460 | 460
| November | 1 | 500 |  |  |  | 1 | 1 |  | 1 | 500 | 1 | 1 |  |  | 0 | 0 | 0 | 0 |  |  | 185 | 185 | 470 | 470
| December | 1 | 500 |  |  |  | 1 | 1 |  | 1 | 500 | 1 | 1 |  |  | 0 | 0 | 0 | 0 |  |  | 185 | 185 | 470 | 470
| Subtract Net CHP and Chiller Offset |  |  | re-check this sector! |  |  | [offset = | 30
| (Finds the units by which to multiply the rates -- accounting for CHP operation [and min-draw requirement] and 10% summer nameplate [on CHP&Energy page]) | [12 empty] | Low case not currently affected by chiller offset b/c assumes zero As-Used anyway
| January | 1 | 500 |  |  |  | 185 | 185 |  | 1 | 500 | 185 | 185 | (This could be changed if a different type of output were desired.)
| February | 1 | 500 |  |  |  | 185 | 185 |  | 1 | 500 | 185 | 185
| March | 1 | 500 |  |  |  | 185 | 185 |  | 1 | 500 | 185 | 185
| April | 1 | 500 |  |  |  | 175 | 175 |  | 1 | 500 | 175 | 175
| May | 1 | 500 |  |  |  | 185 | 185 |  | 1 | 500 | 185 | 185
| June | 1 | 500 |  | 186 | 186 |  |  |  | 1 | 500 | 186 | 186
| July | 1 | 500 |  | 686 | 686 |  |  |  | 1 | 500 | 686 | 686
| August | 1 | 500 |  | 185 | 185 |  |  |  | 1 | 500 | 185 | 185
| September | 1 | 500 |  | 185 | 185 |  |  |  | 1 | 500 | 185 | 185
| October | 1 | 500 |  |  |  | 175 | 175 |  | 1 | 500 | 175 | 175
| November | 1 | 500 |  |  |  | 185 | 185 |  | 1 | 500 | 185 | 185
| December | 1 | 500 |  |  |  | 185 | 185 |  | 1 | 500 | 185 | 185
CALCULATION w/o CHP
| (Rates x Quants) |  |  | Peak Days | Summer | Summer | Winter | Winter | [5 empty] | Low case calculation w/o CHP--not relevant or used; calculation check only | [5 empty] | High case calculation w/o CHP (as-used kW * days * rate)--not relevant or used; calculation check only
| Month | Cust Chg | CD Chg | In Month | As-Use 1 | As-Use 2 | As-Use 1 | As-Use 2 |  |  |  | As Used x Days/Mo. |  | Summer | Summer | Winter | Winter |  |  | Summer | Summer | Winter | Winter
[10 empty] | MAC Cust | MAC CD | MAC AU1 | MAC AU2 | As-Use 1 | As-Use 2 | As-Use 1 | As-Use 2 | MAC AU1 | MAC AU2 | As-Use 1 | As-Use 2 | As-Use 1 | As-Use 2 | MAC AU1 | MAC AU2
| January | 908.12 | 2705 | 22 | 0 | 0 | 0 | 0 |  | 377.1383 | 893.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5376.8 | 0 | 1855.2545
| February | 908.12 | 2705 | 20 | 0 | 0 | 0 | 0 |  | 377.1383 | 893.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4888 | 0 | 1686.595
| March | 908.12 | 2705 | 22 | 0 | 0 | 0 | 0 |  | 377.1383 | 893.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5376.8 | 0 | 1855.2545
| April | 908.12 | 2705 | 21 | 0 | 0 | 0 | 0 |  | 377.1383 | 893.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5023.2 | 0 | 1733.2455
| May | 908.12 | 2705 | 22 | 0 | 0 | 0 | 0 |  | 377.1383 | 893.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5720 | 173.6167 | 1973.675
| June | 908.12 | 2705 | 21 | 0 | 0 | 0 | 0 |  | 377.1383 | 893.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3601.3383 | 7270.011 | 0 | 0 | 166.0564 | 1887.7304
| July | 908.12 | 2705 | 22 | 0 | 0 | 0 | 0 |  | 377.1383 | 893.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7538.1306 | 15217.202 | 0 | 0 | 347.5806 | 3951.2974
| August | 908.12 | 2705 | 22 | 0 | 0 | 0 | 0 |  | 377.1383 | 893.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3765.3 | 7601 | 0 | 0 | 173.6167 | 1973.675
| September | 908.12 | 2705 | 21 | 0 | 0 | 0 | 0 |  | 377.1383 | 893.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3594.15 | 7255.5 | 0 | 0 | 165.725 | 1883.9625
| October | 908.12 | 2705 | 22 | 0 | 0 | 0 | 0 |  | 377.1383 | 893.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5262.4 | 159.7273 | 1815.781
| November | 908.12 | 2705 | 21 | 0 | 0 | 0 | 0 |  | 377.1383 | 893.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5132.4 | 0 | 1770.9248
| December | 908.12 | 2705 | 22 | 0 | 0 | 0 | 0 |  | 377.1383 | 893.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5376.8 | 0 | 1855.2545
| SUM | 10897.44 | 32460 |  | 0 | 0 | 0 | 0 |  | 4525.66 | 10720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18498.9189 | 37343.713 | 0 | 42156.4 | 1186.3227 | 24242.65
[7 empty] | SB Basic | 43357.44 |  |  |  | MAC | 15245.66 |  |  | As-Used Low |  |  | 0 |  |  |  | As-Used High |  | 123428.0046
| CALCULATION w/ CHP | [18 empty] | Should not be affected by demand discount factor
| (Rates x Quants) | [12 empty] | Low case calculation with CHP | [5 empty] | High case calculation with CHP -- using w/o CHP quantities
| January | 908.12 | 2705 | 22 | 0 | 0 | 0 | 11.44 |  | 377.1383 | 893.3333 | 0 | 3.9474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5376.8 | 0 | 1855.2545
| February | 908.12 | 2705 | 20 | 0 | 0 | 0 | 10.4 |  | 377.1383 | 893.3333 | 0 | 3.5885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4888 | 0 | 1686.595
| March | 908.12 | 2705 | 22 | 0 | 0 | 0 | 11.44 |  | 377.1383 | 893.3333 | 0 | 3.9474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5376.8 | 0 | 1855.2545
| April | 908.12 | 2705 | 21 | 0 | 0 | 0 | 10.92 |  | 377.1383 | 893.3333 | 0 | 3.7679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5023.2 | 0 | 1733.2455
| May | 908.12 | 2705 | 22 | 0 | 0 | 0 | 11.44 |  | 377.1383 | 893.3333 | 0.34723 | 3.9474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5720 | 173.6167 | 1973.675
| June | 908.12 | 2705 | 21 | 7.1883 | 14.511 | 0 | 0 |  | 377.1383 | 893.3333 | 0.33145 | 3.7679 | 0 | 0 | 0 | 0 | 0 | 0 | 3601.3383 | 7270.011 | 0 | 0 | 166.0564 | 1887.7304
| July | 908.12 | 2705 | 22 | 7.5306 | 15.202 | 0 | 0 |  | 377.1383 | 893.3333 | 0.34723 | 3.9474 | 0 | 0 | 0 | 0 | 0 | 0 | 7538.1306 | 15217.202 | 0 | 0 | 347.5806 | 3951.2974
| August | 908.12 | 2705 | 22 | 7.5306 | 15.202 | 0 | 0 |  | 377.1383 | 893.3333 | 0.34723 | 3.9474 | 0 | 0 | 0 | 0 | 0 | 0 | 3765.3 | 7601 | 0 | 0 | 173.6167 | 1973.675
| September | 908.12 | 2705 | 21 | 7.1883 | 14.511 | 0 | 0 |  | 377.1383 | 893.3333 | 0.33145 | 3.7679 | 0 | 0 | 0 | 0 | 0 | 0 | 3594.15 | 7255.5 | 0 | 0 | 165.725 | 1883.9625
| October | 908.12 | 2705 | 22 | 0 | 0 | 0 | 11.44 |  | 377.1383 | 893.3333 | 0.34723 | 3.9474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5262.4 | 159.7273 | 1815.781
| November | 908.12 | 2705 | 21 | 0 | 0 | 0 | 10.92 |  | 377.1383 | 893.3333 | 0 | 3.7679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5132.4 | 0 | 1770.9248
| December | 908.12 | 2705 | 22 | 0 | 0 | 0 | 11.44 |  | 377.1383 | 893.3333 | 0 | 3.9474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5376.8 | 0 | 1855.2545
| SUM | 10897.44 | 32460 |  | 29.4378 | 59.426 | 0 | 89.44 |  | 4525.66 | 10720 | 2.0518 | 46.2917 | 0 | 0 | 0 | 0 | 0 | 0 | 18498.9189 | 37343.713 | 0 | 42156.4 | 1186.3227 | 24242.65
[7 empty] | SB CHP | 43535.7438 |  |  |  | MAC | 15294.0035 |  |  |  | As-Used Low |  | 0 |  |  |  | As-Used High |  | 123428.0046
CALCULATION w/ CHP and Chiller Offset
| (Rates x Quants) | [12 empty] | Low case calculation with CHP | [5 empty] | High case calculation with CHP -- chiller offset not relevant here
| January | 908.12 | 2705 | 22 | 0 | 0 | 0 | 2116.4 |  | 377.1383 | 893.3333 | 0 | 730.2598
| February | 908.12 | 2705 | 20 | 0 | 0 | 0 | 1924 |  | 377.1383 | 893.3333 | 0 | 663.8725
| March | 908.12 | 2705 | 22 | 0 | 0 | 0 | 2116.4 |  | 377.1383 | 893.3333 | 0 | 730.2598
| April | 908.12 | 2705 | 21 | 0 | 0 | 0 | 1911 |  | 377.1383 | 893.3333 | 0 | 659.3869
| May | 908.12 | 2705 | 22 | 0 | 0 | 0 | 2116.4 |  | 377.1383 | 893.3333 | 64.2382 | 730.2598
| June | 908.12 | 2705 | 21 | 1337.0238 | 2699.046 | 0 | 0 |  | 377.1383 | 893.3333 | 61.6497 | 700.8341
| July | 908.12 | 2705 | 22 | 5165.9916 | 10428.572 | 0 | 0 |  | 377.1383 | 893.3333 | 238.2021 | 2707.8821
| August | 908.12 | 2705 | 22 | 1393.161 | 2812.37 | 0 | 0 |  | 377.1383 | 893.3333 | 64.2382 | 730.2598
| September | 908.12 | 2705 | 21 | 1329.8355 | 2684.535 | 0 | 0 |  | 377.1383 | 893.3333 | 61.3182 | 697.0661
| October | 908.12 | 2705 | 22 | 0 | 0 | 0 | 2002 |  | 377.1383 | 893.3333 | 60.7658 | 690.7863
| November | 908.12 | 2705 | 21 | 0 | 0 | 0 | 2020.2 |  | 377.1383 | 893.3333 | 0 | 697.0661
| December | 908.12 | 2705 | 22 | 0 | 0 | 0 | 2116.4 |  | 377.1383 | 893.3333 | 0 | 730.2598
| SUM | 10897.44 | 32460 |  | 9226.0119 | 18624.523 | 0 | 16322.8 |  | 4525.66 | 10720 | 550.4122 | 10468.1928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | SB CHP+Chiller | 87530.7749 |  |  |  | MAC | 26264.265 |  |  |  | As-Used Low |  | 0 |  |  |  | As-Used High |  | 0
Note on B5: Low Tension Only!
Note on F5: M-F, 8am - 6pm
Note on G5: M-F, 8am - 10pm
Note on B6: This Row is used by the lookup function -- refers the lookup to appropriate column in MainInterface rates table.
Note on K6: No longer varies depending on NYC v. Westchester: the MAC rates were synchronized per PSC
Note on K7: Estimate of avg. history; note MAC adjustment is volumetric. Used to differ between NYC and Westchester.
Note on M7: MAC Period-1 As-Used charge is not collected in winter months
Note on F22: M-F, 8am - 6pm
Note on G22: M-F, 8am - 10pm
Note on P22: M-F, 8am - 6pm
Note on Q22: M-F, 8am - 10pm
Note on W22: M-F, 8am - 6pm
Note on X22: M-F, 8am - 10pm
Note on AA22: Uses non-discounted monthly peak; Period 2 uses same as P 1, but likely is lower
Note on A23: CY: Info Only: selected discount from monthly peak
Note on H24: CY: (Monthly peak) x ("Peak Reduction Factor") = Assumed As-Used Level
Note on M24: MAC Period-1 As-Used charge is not collected in winter months
Note on P24: "Low Case" assumes that all as-used charges are obviated by perfect operation of the CHP and/or zero underlying demand.
Note on Y24: CY: NOT discounted from monthly peak for "high case" computation.
Note on H40: T4 - T15 = "Net Output" of DG, after parasitics. Net Output is not named so users can change the parasitics by season if desired.
Note on P40: This block is not relevant for low case calculation, because assumes 100% CHP operation.
Note on W40: This block not relevant for high case; assume CHP offset = 0
Note on H56: (Monthly peak) x ("Peak Reduction Factor") = Assumed As-Used Level
Note on W71: Should not be affected by demand discount factor!
Note on P73: M-F, 8am - 6pm
Note on Q73: M-F, 8am - 10pm
Note on W73: M-F, 8am - 6pm
Note on X73: M-F, 8am - 10pm
Note on E74: Data in "Tables" sheet
Note on AB88: Output to High Case - assumes that CD is 100% of monthly peak, every day.
Note on E92: "Days" data in "Tables" sheet
Note on U106: CY: Would Output to "boundary" in if we were using CHP offset as the low boundary. B/C using zero as-used, output is below (zero).
Note on E111: "Days" data in "Tables" sheet
Note on U125: CY: Output to "low" boundary; b/c assumes zero as-used charges, this should be zero.

## Issues
Notes, Errors, Manual Additions, Etc.
Pink | Returns information from spreadsheet (e.g., from inputs or other worksheets); helps with debugging
Red | Notes or errors to address/correct
Blue | Informational cells used in the calculation, lookup references, etc.
Plum | Settings for advanced users
Green | Information note or possible error; not critical; info for possible modificaton
Sources of inaccuracy
MAC estimates and adjustments
energy cost assumptions
estimation of as-used demand
demand period "overlap" P1 to P2
Reiterate that the MAC is hard to estimate
usage assumptions/variations
unpredictable weather (possibility of weather normalization using Itron?)
seasonal and other variation
Does not included taxes
Does not compute minimum charges (I.e., 10 kW in SC-8)
Does not compute surcharges for exceeding contract demand -- Explain in manual
Reactive Power is not accounted for in this spreadsheet.
No fuel price information, so does not show the great economic advantages of greater efficiency
Rates will change over time -- especially the MAC -- and users should be aware (and check the update history)
-> Manual states where to find current rates to double-check if it's not recent
Interconnection Assessment is not accounted for in this spreadsheet (Note depends on date of IC; see below)
(varies if +/- 2 MW, after '04, SIR applies, etc.) See "inaccuracies" below.
Applicability – Rate II
A Customer who would otherwise receive service under Service Classification No. 4, 5, 8, 9, or 12 will be
subject to the rates shown for Customers who would be subject to Rate II of the applicable Service
Classification under the following conditions:
(a) where the Customer’s Contract Demand is greater than 1500 kW;
(b) where the Customer’s Contract Demand is greater than 900 kW and the Customer takes service under Rider J of the Full Service Schedule; and
(c) where the Customer would receive service under Special Provision H of Service Classification No. 4, 8, 9, or 12.
Where high tension service is supplied at 138,000 volts, the Customer will be subject to the rate shown for high tension service at 138 kV rate regardless of the Contract Demand.
All other Customers who would otherwise receive service under Service Classification No. 4, 5, 8, 9, or 12 will be billed at the rate shown for Customers who would not be subject to Rate II.